## BOM
JAIN GRANITE & MARBLE — 100.00 kWp ROOFTOP: BILL OF MATERIAL (STRINGING, DC CABLE, MC4, CABLE TRAY, WALKWAY)
BOM v1 · 27-10-2026 · based on drawings v5 (06 Stringing, 05 Cable Tray, 04 Walkway) · 160 x Adani AB-G12R-132-625, GoodWe GW80K-MT, 8 strings x 20, no Y-connectors
Quantities marked * depend on lengths scaled from the layout photo — confirm with a site measurement before ordering.
S.No | Item | Specification | Unit | Calculated qty | Qty to order | Rate (₹) | Amount (₹) | Basis / note
A. DC CABLE (STRING HOME RUNS + ROW-TURN JUMPERS)
A1 | DC solar cable 4 sq mm – RED (+VE) | 1C x 4 sq mm Cu, EN 50618 / H1Z2Z2-K, 1.5 kV DC, UV & XLPO | m | 310.8 | 330 | 58 |  | Sum of 8 +VE home runs along tray route (see sheet "DC cable by string") + 5 %. *
A2 | DC solar cable 4 sq mm – BLACK (–VE) | Same as A1 | m | 368.4 | 390 | 58 |  | Sum of 8 –VE home runs + 5 %. –VE runs are longer (row 4 / row 8 terminals). *
A3 | DC solar cable 4 sq mm – row-turn jumpers | Same as A1 (either colour) | m | 60 | 65 | 58 |  | 24 jumpers (3 row turns x 8 strings) x 2.5 m. Module pitch 2.4 m in portrait; module leads do not reach. Drop if modules are ordered with long (≥ 1.2 m) leads that reach across the turn.
B. MC4 CONNECTORS
B1 | MC4 connector pair – array end of home runs | 1 male + 1 female, 1500 V DC, 4–6 sq mm, IP68, SAME MAKE/TYPE AS MODULE CONNECTORS | pair | 8 | 8 |  |  | 16 conductors x 1 connector each at the array end = 16 halves = 8 pairs (one +, one – per string).
B2 | MC4 connector pair – row-turn jumpers | Same as B1 | pair | 24 | 24 |  |  | 1 pair per jumper (one end each). Not needed if A3 is dropped.
B3 | MC4 connector pair – spares | Same as B1 | pair |  | 4 |  |  | ≈ 10 % spare for re-termination on site.
B4 | DC connectors – inverter end | GoodWe-supplied DC connectors (in the inverter box) | pair | 8 | 0 |  |  | 8 pairs needed (2 inputs x 4 MPPT). Use the GoodWe connectors supplied with the inverter (warranty / compatibility). Order 8 pairs of the inverter-compatible type ONLY if the box does not include them.
B5 | MC4 crimping tool + spanner set | For 2.5 / 4 / 6 sq mm contacts | set |  | 1 |  |  | Skip if the site team already has one.
C. DC CABLE TRAY (SHEET 05)
C1 | Perforated cable tray 100 x 50 mm | HDG, 1.6 mm, standard 2.5 m lengths | length (2.5 m) | 75.9 | 34 |  |  | Route T1 + T2 + T3a + T3b + T4 = 75.9 m (see "Tray & walkway runs") + 10 % = 85.0 m. *
C2 | Tray cover 100 mm | HDG, bolted / clip-on, 2.5 m | length (2.5 m) |  | 34 |  |  | Full length — UV and bird / monkey protection.
C3 | Flat 90° bend 100 x 50 | HDG | no. | 2 | 2 |  |  | T1 → north edge; wall vertical → along wall.
C4 | Tee 100 x 50 | HDG | no. | 1 | 1 |  |  | T2 joining the north-edge run.
C5 | Vertical (riser) bend 100 x 50 | HDG | no. | 2 | 2 |  |  | Over the east eave onto the wall; down into the inverter.
C6 | Tray coupler / joint set | With bolts, nuts, washers | set | 38 | 40 |  |  | One per joint between lengths and at each fitting end, + 5 %.
C7 | End cap 100 x 50 | HDG | no. | 2 | 2 |  |  | South ends of T1 and T2.
C8 | Roof tray support / purlin clamp (75–100 mm raised) | HDG, with EPDM-sealed fixings | no. | 46 | 48 |  |  | Every 1.5 m on 62.0 m of roof tray + run ends. *
C9 | Wall bracket for tray | HDG, anchor-fixed | no. | 13 | 14 |  |  | Every 1.2 m on the 13.9 m wall run (T4). *
C10 | Tray earth-continuity jumper | 6 sq mm Cu with lugs (or couplers rated for continuity) | no. | 38 | 38 |  |  | Across each joint, so the whole tray bonds to EP-1.
C11 | Cable ties, UV-stabilised | 300 mm and 200 mm, black | pack of 100 |  | 6 |  |  | Home runs in the vertical wall tray (every 0.5 m) + clipping module leads / jumpers to rails. Estimate.
C12 | Cable markers | Printed / ferrule, S1+ … S8– | no. | 32 | 40 |  |  | Both ends of all 16 home-run conductors (32) + spare.
D. WALKWAY (SHEET 04)
D1 | Walkway 300 mm wide | FRP or HDG anti-skid grating, UV-stabilised, ≥ 150 kg/m² | m | 75.5 | 80 |  |  | W1 + W2 + WC + WA1 + WA2 = 75.5 m + 5 %. In 3 m panels: 27 panels. *
D2 | Walkway fixing clamp / support set | Purlin clamp, no sheet puncture (or EPDM-sealed) | set | 63 | 67 |  |  | Every 1.2 m (confirm purlin spacing on site). *
D3 | Lifeline / handrail at ladder landing | Along WA2 (south eave) + ladder landing | m | 6.6 | 9 |  |  | Only stretch of walkway near a roof edge.
E. RELATED – IN THE SAME TRAY (OPTIONAL, FROM EARTHING LAYOUT)
E1 | Earth cable 16 sq mm Cu (green / yellow) | PV structure earth bus, laid in the DC tray | m | 80.9 | 90 |  |  | Tray route + ≈ 5 m from the wall to EP-1, + 10 %. *
| TOTAL (items with a rate) | [6 empty] | Fill in rates in column G for the rest.

## DC cable by string
String | MPPT | Input | Slope | +VE red (m) | –VE black (m) | Pair (m) | How it is measured
S1 | 3 | 1 | West | 42.1 | 49.3 | 91.5 | terminal row → tray in the block gap → north edge → east eave → 10 m down the wall → along wall to inverter, + 1.0 m array tail + 1.5 m at inverter
S2 | 4 | 1 | West | 51.7 | 59 | 110.7 | terminal row → tray in the block gap → north edge → east eave → 10 m down the wall → along wall to inverter, + 1.0 m array tail + 1.5 m at inverter
S3 | 3 | 2 | West | 42.1 | 49.3 | 91.5 | terminal row → tray in the block gap → north edge → east eave → 10 m down the wall → along wall to inverter, + 1.0 m array tail + 1.5 m at inverter
S4 | 4 | 2 | West | 51.7 | 59 | 110.7 | terminal row → tray in the block gap → north edge → east eave → 10 m down the wall → along wall to inverter, + 1.0 m array tail + 1.5 m at inverter
S5 | 1 | 1 | East | 25.9 | 33.1 | 59.1 | terminal row → tray in the block gap → north edge → east eave → 10 m down the wall → along wall to inverter, + 1.0 m array tail + 1.5 m at inverter
S6 | 2 | 1 | East | 35.5 | 42.8 | 78.3 | terminal row → tray in the block gap → north edge → east eave → 10 m down the wall → along wall to inverter, + 1.0 m array tail + 1.5 m at inverter
S7 | 1 | 2 | East | 25.9 | 33.1 | 59.1 | terminal row → tray in the block gap → north edge → east eave → 10 m down the wall → along wall to inverter, + 1.0 m array tail + 1.5 m at inverter
S8 | 2 | 2 | East | 35.5 | 42.8 | 78.3 | terminal row → tray in the block gap → north edge → east eave → 10 m down the wall → along wall to inverter, + 1.0 m array tail + 1.5 m at inverter
TOTAL
Row-turn jumpers | [5 empty] | 60 | 24 x 2.5 m (3 per string)

## Tray & walkway runs
Run | Route | Length (m) | Contents / width
T1 | GAP BLOCK 1/2: ROW 8 → NORTH EDGE | 19.3 | 8 x 4 SQ MM + 16 SQ MM E (S1–S4)
T2 | GAP BLOCK 3/4: ROW 8 → NORTH EDGE | 19.3 | 8 x 4 SQ MM + 16 SQ MM E (S5–S8)
T3a | NORTH EDGE: T1 → T2 (OVER RIDGE) | 16.2 | 8 x 4 SQ MM + 16 SQ MM E (S1–S4)
T3b | NORTH EDGE: T2 → EAST EAVE | 7.15 | 16 x 4 SQ MM + 16 SQ MM E (ALL 8 STRINGS)
T4 | EAST WALL: DOWN 10 m + ALONG TO INVERTER | 13.9 | 16 x 4 SQ MM + 16 SQ MM E (ALL 8 STRINGS)
| TOTAL DC TRAY | 75.85 | 100 x 50 mm
W1 | WEST SLOPE: GAP BLOCK 1 / 2 (BESIDE T1) | 19.2 | 300 mm
W2 | EAST SLOPE: GAP BLOCK 3 / 4 (BESIDE T2) | 19.2 | 300 mm
WC | Connector, just south of the arrays, W1 → W2 | 16.5 | 300 mm
WA1 | Access: W1 continued south to the access strip * | 13.95 | 300 mm
WA2 | Access: along the south edge from the SW ladder * | 6.62 | 300 mm
| TOTAL WALKWAY | 75.47 | 300 mm